## Instrucciones
Modulo Transformadores

## TR
Load | Temp | Type | ID | Serial | Location | Opt_Year | Brand | Model | U_max | S | I_LV | Paper_Therm_Up | Oil | ONAF_I | ONAF_II | Top_Oil | Avg_Wing | Ta | Material | Windings | Phases | Connection | Z | Oil_Litters | Mass_Core | Mass_Tank | Po | i2R | Stray_Losses | Eddy_Losses | Top_Oil | Bot_Oil | Avg_Wing | dTheta_TO_R | Gradient | UC
TR1 | 25 | TR | TR_0_1 | 4 | BOG_1 | 1993 | Siemens | AT | 345 | 700 | 24.52 | FALSE | Mineral | 1.25 | 1.5 | 55 | 19.6 | 2.5 | Cooper | 2 | 3 | YNy0 | 0.1306 | 855 | 245 | 132 | 0 | 0 | 0 | 0 | 55 | 33 | 60 | 0 | 14.85 | N5S2
TR2 | 25 | TR | TR_0_12 | 5 | BOG_2 | 1993 | Siemens | AT | 345 | 1000 | 35.03 | FALSE | Mineral | 1.25 | 1.5 | 55 | 19.6 | 2.5 | Cooper | 2 | 3 | YNy0 | 0.1306 | 1083 | 424 | 156 | 0 | 0 | 0 | 0 | 55 | 33 | 60 | 0 | 14.85 | N5S2

## DGA
Test_ID | Pos | Serial | Location | Date | H | O | N | CO | CH4 | CO2 | C2H4 | C2H6 | C2H2 | TDCG
1 | TR_0_1 | 4 | Bog | 2015-03-18 | 0.57067 | 2415.335 | 5533.374 | 3.0872 | 0 | 41.7234 | 0 | 0 | 0 | 44.8106
2 | TR_0_1 | 4 | Bog | 2015-04-17 | 0.82105 | 4584.237 | 10761.9 | 7.2413 | 0 | 85.6772 | 0 | 0 | 0 | 92.9185
3 | TR_0_1 | 4 | Bog | 2015-04-22 | 1.8923 | 5461.517 | 13580.86 | 10.2169 | 0.40351 | 105.828 | 0 | 0 | 0 | 116.4484
4 | TR_0_1 | 4 | Bog | 2015-12-09 | 2.3899 | 3848.962 | 12761.75 | 30.0782 | 0 | 145.6121 | 0 | 0 | 0 | 175.6903
5 | TR_0_1 | 4 | Bog | 2016-06-16 | 4.0084 | 10262.94 | 37083.49 | 95.4701 | 0 | 405.5897 | 0 | 0 | 0 | 501.0598
6 | TR_0_1 | 4 | Bog | 2017-05-04 | 10.1757 | 9694.103 | 31035.57 | 107.5745 | 1.3206 | 393.0207 | 0 | 0 | 0 | 501.9158
7 | TR_0_1 | 4 | Bog | 2018-02-26 | 8.3853 | 17028.45 | 39088.48 | 157.1902 | 2.2192 | 565.6402 | 0.22508 | 0.91685 | 0 | 726.1915
8 | TR_0_12 | 5 | Bog | 2007-01-22 | 31.1792 | 18586.15 | 38981.54 | 82.288 | 6.8634 | 1147.982 | 12.0949 | 1.025 | 96.3539 | 1346.6072
9 | TR_0_12 | 5 | Bog | 2007-02-06 | 28.4944 | 16201.13 | 34120 | 70.3635 | 6.222 | 1082.572 | 11.7269 | 0.70742 | 96.3708 | 1267.9625
10 | TR_0_12 | 5 | Bog | 2007-04-09 | 30.4279 | 17113.73 | 39527.61 | 72.5519 | 7.6095 | 1281.556 | 14.2476 | 1.354 | 145.6573 | 1522.9763
11 | TR_0_12 | 5 | Bog | 2007-04-24 | 31.0297 | 18535.05 | 39992.83 | 67.3507 | 8.0545 | 1269.502 | 15.8339 | 1.5511 | 146.6431 | 1508.9353
12 | TR_0_12 | 5 | Bog | 2007-05-16 | 32.7298 | 17171.66 | 40631.14 | 67.183 | 8.4529 | 1300.704 | 16.3172 | 1.5722 | 158.7835 | 1553.0127
13 | TR_0_12 | 5 | Bog | 2007-06-22 | 33.8229 | 18569.83 | 43417.21 | 74.054 | 8.9826 | 1405.558 | 17.8033 | 1.7852 | 162.2863 | 1670.4694
14 | TR_0_12 | 5 | Bog | 2007-07-06 | 31.8801 | 18487.59 | 42721.2 | 70.9453 | 8.8377 | 1408.122 | 18.5767 | 1.904 | 167.1672 | 1675.5529
15 | TR_0_12 | 5 | Bog | 2007-09-11 | 27.4051 | 14225.96 | 32385.48 | 62.2589 | 7.0616 | 1219.61 | 15.8614 | 1.5832 | 152.9844 | 1459.3594
16 | TR_0_12 | 5 | Bog | 2007-12-13 | 25.9656 | 15067.54 | 36020.55 | 67.9608 | 7.6814 | 1098.592 | 18.3151 | 1.7642 | 156.9507 | 1351.2642
17 | TR_0_12 | 5 | Bog | 2008-04-24 | 28.1053 | 17380.62 | 43368.37 | 73.7785 | 8.4242 | 1310.439 | 18.3718 | 2.4184 | 184.1459 | 1597.5777
18 | TR_0_12 | 5 | Bog | 2008-05-22 | 20.6258 | 17682.55 | 40756.4 | 66.0841 | 7.308 | 1269.509 | 19.568 | 1.9636 | 175.0419 | 1539.4746
19 | TR_0_12 | 5 | Bog | 2008-06-16 | 17.9449 | 17011.15 | 38795.5 | 59.0381 | 5.9934 | 1210.553 | 15.543 | 1.5739 | 147.9752 | 1440.6766
20 | TR_0_12 | 5 | Bog | 2008-08-20 | 11.6748 | 17935.81 | 44100.82 | 69.2386 | 5.2133 | 1323.451 | 14.8343 | 1.4612 | 149.5574 | 1563.7557
21 | TR_0_12 | 5 | Bog | 2008-12-09 | 10.1966 | 18085.36 | 42964.14 | 74.7904 | 4.0763 | 1477.29 | 17.0543 | 1.8672 | 156.8506 | 1731.9289
22 | TR_0_12 | 5 | Bog | 2009-03-20 | 11.0438 | 17529.16 | 43302.61 | 98.7977 | 3.7742 | 1563.81 | 14.1552 | 1.5732 | 144.1281 | 1826.2384
23 | TR_0_12 | 5 | Bog | 2010-04-26 | 15.7617 | 19155.04 | 47255.63 | 108.3558 | 4.4209 | 1704.202 | 13.8298 | 1.6115 | 78.3489 | 1910.7689
24 | TR_0_12 | 5 | Bog | 2010-11-08 | 17.377 | 18592.7 | 43485.28 | 65.1475 | 4.0652 | 1577.711 | 12.6088 | 1.5255 | 83.2184 | 1744.2763
25 | TR_0_12 | 5 | Bog | 2011-12-01 | 18.9872 | 18690.34 | 42710.61 | 55.0992 | 4.5466 | 1282.835 | 12.4342 | 1.6948 | 78.093 | 1434.7028
26 | TR_0_12 | 5 | Bog | 2013-05-16 | 6.2346 | 18020.19 | 43032.46 | 51.1489 | 1.6442 | 1103.308 | 5.8288 | 0.21467 | 29.8609 | 1192.0055
27 | TR_0_12 | 5 | Bog | 2014-03-31 | 5.4686 | 20060.42 | 43713.61 | 0 | 0.001 | 1017.068 | 5.9486 | 1.0234 | 28.1911 | 1052.2321
28 | TR_0_12 | 5 | Bog | 2015-06-03 | 7.356 | 18935.04 | 42720.09 | 53.6182 | 1.8091 | 978.1443 | 4.4552 | 0.99664 | 20.1442 | 1059.1676
29 | TR_0_12 | 5 | Bog | 2016-07-06 | 8.3734 | 18091.69 | 46939.96 | 55.6828 | 0 | 1079.953 | 9.1887 | 26.2973 | 15.502 | 1186.6238
30 | TR_0_12 | 5 | Bog | 2017-05-10 | 12.6905 | 11520.18 | 50781 | 89.3315 | 2.3693 | 1346.888 | 5.2542 | 2.4007 | 16.0312 | 1462.2749
31 | TR_0_12 | 5 | Bog | 2018-08-24 | 4.3974 | 5981.839 | 4516.491 | 13.74 | 0 | 1335.472 | 1.5996 | 1.5863 | 0 | 1352.3979
Note on N1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Todas las concentraciones de gases deben ir en ppm
Note on O1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Todas las concentraciones de gases deben ir en ppm

## PQ
Test_ID | Pos | Serial | Location | Date | C_H2O | Sat | Color | IT | DS | AN
1 | TR_0_1 | 4 | Bog | 2015-03-19 | 4.9 | 9 | 0.5 | 46.1525 | 39.9 | 0.013
2 | TR_0_1 | 4 | Bog | 2015-04-27 | 3.3 | 3 | 0.5 | 42.8367 | 46.48 | 0.01
3 | TR_0_1 | 4 | Bog | 2015-04-27 | 2.7 | 3 | 0.5 | 41.7466 | 39.42 | 0.015
4 | TR_0_1 | 4 | Bog | 2015-12-09 | 2.5 | 2 | 0.5 | 40.4658 | 51.98 | 0.009
5 | TR_0_1 | 4 | Bog | 2016-06-21 | 3.8 | 3 | 0.5 | 45.1993 | 46.18 | 0.004
6 | TR_0_1 | 4 | Bog | 2017-05-08 | 8.1 | 7 | 0.5 | 47.1653 | 29.06 | 0.005
7 | TR_0_1 | 4 | Bog | 2018-03-01 | 2.7 | 2 | 0.5 | 37.7674 | 51.34 | 0.005
8 | TR_0_1 | 4 | Bog | 2019-03-18 | 3.7 | 4.101 | 0.5 | 38.55 | 33.3 | 0.006
9 | TR_0_12 | 5 | Bog | 2007-01-23 | 8.1 | 7 | 1 | 29.5504 | 34.46 | 0.009
10 | TR_0_12 | 5 | Bog | 2008-05-21 | 8.3 | 7 | 1 | 31.4985 | 33.22 | 0.009
11 | TR_0_12 | 5 | Bog | 2008-08-26 | 7.9 | 7 | 1 | 30.1513 | 41.58 | 0.01
12 | TR_0_12 | 5 | Bog | 2009-04-30 | 11.9 | 8 | 1.5 | 29.8074 | 36 | 0.017
13 | TR_0_12 | 5 | Bog | 2010-04-27 | 14.3 | 10 | 1.5 | 26.7033 | 35.04 | 0.018
14 | TR_0_12 | 5 | Bog | 2011-12-14 | 9.3 | 8 | 1.5 | 27.7908 | 39.64 | 0.014
15 | TR_0_12 | 5 | Bog | 2013-05-30 | 9.5 | 6 | 1.5 | 29.2073 | 39.88 | 0.018
16 | TR_0_12 | 5 | Bog | 2014-04-21 | 9.5 | 8 | 1.5 | 27.3309 | 44.4 | 0.016
17 | TR_0_12 | 5 | Bog | 2015-06-11 | 9.1 | 8 | 1.5 | 27.8563 | 35.64 | 0.038
18 | TR_0_12 | 5 | Bog | 2016-07-06 | 10.8 | 8 | 1.5 | 26.1158 | 29.5 | 0.017
19 | TR_0_12 | 5 | Bog | 2017-05-11 | 10.1 | 8 | 1.5 | 29.2181 | 20.62 | 0.02
Note on F1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Contenido de agua (mg/kg)
Note on G1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Saturación en %
Note on H1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Color (sin unidades)
Note on I1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Tensión interfacial en (mN/m)
Note on J1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Rigidez dieléctrica en (kV)
Note on K1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Número ácido en (mg KOH/g)

## FURANS
Test_ID | Pos | Serial | Location | Date | F_5H2F | F_2FOL | F_2FAL | F_2ACF | F_5M2F
1 | TR_0_1 | 4 | Bog | 2015-04-22 | 0 |  | 20 | 0 | 6
2 | TR_0_1 | 4 | Bog | 2015-06-17 | 0 |  | 19 | 0 | 0
3 | TR_0_1 | 4 | Bog | 2015-06-17 | 0 |  | 11 | 0 | 0
4 | TR_0_1 | 4 | Bog | 2015-12-12 | 0 |  | 5 | 0 | 7
5 | TR_0_1 | 4 | Bog | 2017-07-13 | 0 |  | 0 | 0 | 0
6 | TR_0_1 | 4 | Bog | 2018-06-21 | 0 | 0 | 0 | 0 | 0
7 | TR_0_1 | 4 | Bog | 2019-03-18 | 0 | 91 | 0 | 0 | 0
8 | TR_0_12 | 5 | Bog | 2012-02-17 | 4 | 609 | 167 | 0 | 0
9 | TR_0_12 | 5 | Bog | 2013-09-06 | 0 | 0 | 544 | 0 | 0
10 | TR_0_12 | 5 | Bog | 2014-05-26 | 0 |  | 428 | 0 | 0
11 | TR_0_12 | 5 | Bog | 2015-06-18 | 0 |  | 590 | 0 | 0
12 | TR_0_12 | 5 | Bog | 2017-07-17 | 0 |  | 112 | 0 | 0
13 | TR_0_12 | 5 | Bog | 2019-01-11 | 0 | 260 | 204 | 35 | 0

## Electric_Test
Test_ID | Pos | Serial | Location | Date | PF | IP | WR | IR | TR
1 | TR_2 | 2 | TR_2 | 2014-03-31 | 0.1 | 2 | 0.9 | 650 | 0.1
2 | TR_2 | 2 | TR_2 | 2015-06-03 | 0.25 | 1.1 | 1 | 500 | 0.2
3 | TR_2 | 2 | TR_2 | 2016-07-06 | 1.2 | 1.75 | 2 | 450 | 0.3
4 | TR_2 | 2 | TR_2 | 2017-05-10 | 1.5 | 1.5 | 1.25 | 5 | 0.5
5 | TR_2 | 2 | TR_2 | 2013-05-16 | 1.6 | 1.5 | 1.3 | 50 | 0.6
6 | TR_4 | 4 | TR_4 | 2013-03-08 | 0.1 | 2 | 0.9 | 650 | 0.1
7 | TR_4 | 4 | TR_4 | 2013-03-21 | 0.25 | 1.1 | 1 | 500 | 0.2
8 | TR_4 | 4 | TR_4 | 2013-03-21 | 1.2 | 1.75 | 2 | 450 | 0.3
9 | TR_4 | 4 | TR_4 | 2014-02-06 | 1.5 | 1.5 | 1.25 | 5 | 0.5
10 | TR_4 | 4 | TR_4 | 2017-01-04 | 1.6 | 1.5 | 1.3 | 50 | 0.6
Note on F1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Factor de potencia en p.u.
Note on G1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Polarización
Note on H1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Resistencia de los devanados en % de fábrica
Note on I1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Resistencia de aislamiento en MΩ
Note on J1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Relación de transformación en % de error

## OPERATION
Test_ID | Pos | Serial | Location | Date | LF | AT | HS | A | Replacement
1 | TR2 | 39TR2 | TR2 | 2017-05-11 | 0.8 | 24 | 90 | 0 | TRUE
2 | TR2 | 39TR2 | TR2 | 2016-07-06 | 0.9 | 23 | 95 | 0 | TRUE
3 | TR2 | 39TR2 | TR2 | 2015-06-11 | 1 | 24 | 100 | 0 | TRUE
4 | TR2 | 39TR2 | TR2 | 2014-04-21 | 1.1 | 22 | 100 | 0 | TRUE
5 | TR2 | 39TR2 | TR2 | 2013-05-30 | 1 | 23 | 98 | 0 | TRUE
6 | TR4 | 39TR4 | TR4 | 2017-02-16 | 1 | 20 | 100 | 0 | FALSE
7 | TR4 | 39TR4 | TR4 | 2014-02-06 | 1.2 | 21 | 110 | 0 | FALSE
8 | TR4 | 39TR4 | TR4 | 2013-04-09 | 1.2 | 21 | 105 | 0 | FALSE
9 | TR4 | 39TR4 | TR4 | 2013-04-09 | 1.5 | 21 | 105 | 0 | FALSE
10 | TR4 | 39TR4 | TR4 | 2013-04-09 | 1.2 | 23 | 100 | 0 | FALSE

## OLTC_Test
Test_ID | Pos | Serial | Location | Date | NO | YS
1 | TR2 | 39TR2 | TR2 | 2017-05-11 | 230000 | 44
2 | TR2 | 39TR2 | TR2 | 2016-07-06 | 200000 | 43
3 | TR2 | 39TR2 | TR2 | 2015-06-11 | 180000 | 42
4 | TR2 | 39TR2 | TR2 | 2014-04-21 | 160000 | 41
5 | TR2 | 39TR2 | TR2 | 2013-05-30 | 150000 | 40
6 | TR4 | 39TR4 | TR4 | 2017-02-16 | 250000 | 24
7 | TR4 | 39TR4 | TR4 | 2014-02-06 | 200000 | 21
8 | TR4 | 39TR4 | TR4 | 2013-04-09 | 180000 | 20
9 | TR4 | 39TR4 | TR4 | 2013-04-09 | 180000 | 20
10 | TR4 | 39TR4 | TR4 | 2013-04-09 | 180000 | 20

## Bushing_Test
Test_ID | Pos | Serial | Location | Date | PF_B | C
1 | TR2 | 39TR2 | TR2 | 2017-05-11 | 0.7 | 1
2 | TR2 | 39TR2 | TR2 | 2016-07-06 | 0.6 | 0.75
3 | TR2 | 39TR2 | TR2 | 2015-06-11 | 0.6 | 0.7
4 | TR2 | 39TR2 | TR2 | 2014-04-21 | 0.5 | 0.6
5 | TR2 | 39TR2 | TR2 | 2013-05-30 | 0.45 | 0.5
6 | TR4 | 39TR4 | TR4 | 2017-02-16 | 0.7 | 1
7 | TR4 | 39TR4 | TR4 | 2014-02-06 | 0.6 | 0.75
8 | TR4 | 39TR4 | TR4 | 2013-04-09 | 0.6 | 0.7
9 | TR4 | 39TR4 | TR4 | 2013-04-09 | 0.5 | 0.6
10 | TR4 | 39TR4 | TR4 | 2013-04-09 | 0.45 | 0.5

## Criticality_Test
Test_ID | Pos | Serial | Location | Date | ENS (MWh) | MMTR (hrs) | MMTF (hrs) | PCB
1 | TR2 | 39TR2 | TR2 | 2017-05-11 | 12 | 400 | 24 | TRUE
2 | TR4 | 39TR4 | TR4 | 2017-02-16 | 5 | 336 | 15 | TRUE

## _56F9DC9755BA473782653E2940F9 (hidden)
2MF_VyIJjkWHv-xPRV62AFp6FmJGvDJDlaNXvDlwm8NUQVQ5TFVKRllOUTRMWlBJS0syOUhLSFNOVi4u
Form1
{dcbd5c6e-e310-4cb1-a15e-380c47f2a6be}